## Slide 1: Deployment of Rapid Control Prototyping Technique for 3-phase Inverters
Final Year Project Presentation
Yan To Chau (01705211)
Wednesday, 28 June 2023
1
Notes: Deployment of RCP (rapid control prototyping for 3-phase inverter)
Before we go any further: quick look at the final hardware produced for the project, which is shown in a system level diagram later
Overview: Intro, 3 main concepts, tests and demo

## Slide 2: GFM (Forming) vs GFL (Following) Inverters
GFM: Tracks a grid voltage and frequency reference regardless of DC voltage or load variations
  UPS (uninterruptible supply): supplying to loads of an isolated network
GFL: Tracks a current reference, control power exchange
  Example: Connections of PV farm or ESS to an AC grid
Switch between modes.
Introduction
1/1
2
Notes: An IBR connected to an AC grid (with little synchronous generation) can switch between GFM and GFL mode.
GFM: start from black out to initialise a stiff grid voltage
GFL: then when the grid is stable or when the system inertia is built it can run in GFL to maximise power.
As shown in the diagram
GFL: current control
GFM: outer loop voltage control and inner loop current control
Current control offers control over power, and also limits the current at switches
Switch between GFM and GFL modes: for example, startup of an AC grid from black-out, using an IBR (inverter-based resource)

## Slide 3: Inverter Hardware
3 Phase DC-AC half bridge
LCL Filter
CMC (Common Mode Choke)
Hardware
1/1
3
Notes: NO MORE THAN 10 SECONDS
3 parts of an inverter that I will not go in detail today
Inverter: Formed by 3 single-phase DC-AC half bridge.
LCL filter: Comparison between this and L and LC filter: Further ripple current attenuation by grid side inductor, capacitor that absorbs high frequency currents (reactive power)
CMC: Cancels out CM voltage which is the difference in voltage between the DC ground and capacitor neutral.

## Slide 4: Reference Frames
abc (stationary): 3 balanced quantities in a stationary co-planar frame
αβ (natural): 2 orthogonal quantities in a stationary orthogonal frame
dq (synchronous): 2 DC orthogonal quantities in a rotating orthogonal frame
Dynamics
1/2
4
Notes: (Before I talk about Plant Equations)
Reference frames is important
Stationary frame to control (hard to control sinusoidally varying waveform)
Draw attention to dq -> 2 DC orthogonal quantities in a rotating orthogonal frame
Because tracking signal is DC, reference can be DC too, making it much easier to control.
Hard to control 3 coupled signals
PLL ensures it rotates at the correct speed and phase

## Slide 5: Inverter Plant Equations: LC
Dynamics
2/2
5
Notes: inductor current dynamics
capacitor voltage dynamics
Plant equations in space vector and in dq form.
Forms the basis for control

## Slide 6: Inverter Control
GFL PLL, PI Controller
GFL Current Controller (and GFM inner-loop current controller)
GFL Power to Current Reference Conversion
GFL Overview
GFM Voltage Controller
GFM Overview
Control
0/5
6
Notes: DO NOT READ EVERYTHING ON THID SLIDE
GFL features: current controller, PLL
GFM: voltage controller and current controller from GFL

## Slide 7: GFL Power to Current Reference Conversion
Control
1/5
7
Notes: Finally with the power to current reference conversion this completes the GFL control
Because we have a current control strategy – inductor current dynamics plant model

## Slide 8: GFL PLL (Phase-Locked Loop)
Synchronises dq-frame rotation with grid: angular velocity ω and phase ρ
Correct q-component of Vc with PI Controller
LPF for attenuation
VCO (voltage-controlled oscillator/ integrator) centred at 50Hz
Phase generated feeds to abc-dq dq-abc blocks
Control
2/5
8
Notes: PI controller chosen based on loop shaping method
  Unity loop gain
  Separation between cutoff and crossover frequency
LPF: for a stable attenuated response

## Slide 9: GFL Current Control
Convert to dq-frame
PI-Controller and cross-decoupling
Convert to abc-frame and modulation
Control
3/5
9

## Slide 10: GFM Overview
Control
4/5
10
Notes: This completes the GFM control setup

## Slide 11
11
Notes: And in combination we can operate a transmission line formed by 2 inverters, control its voltage, and control power flow

## Slide 12: System Overview
Implementation
1/1
12
Notes: This describes the diagram previously shown: how GFM and GFL can be tested separately and operated together in cosed loop

## Slide 13: Tests Overview
Rationale and results for tests
Open-Loop
GFL
GFM
Dual (GFM and GFL)
Results
0/4
13
Notes: Now I will go through each of the tests listed on this slide
Rationale: why this test is performed
Results: what this has yielded

## Slide 14: Open-Loop
Check abc (sinusoidal) waveforms
Calibration, debugging, check ADC protection
PLL: Check stability of dq-results (not tracking)
Results
1/4
14
Notes: Rule of thumb checks
Calibration:
  fixing absolute errors,
  checking definitions such as power and current definitions (which should be in generator convention), order of phases
  Mismatch between zero points will lead to 50Hz oscillations
As expected
  All sinusoidal waveforms, filtered version,
  50HZ Dominant
  PLL: check whether dq results are stable. Correspond to the amplitude (power invariant transform)
  Some high frequency oscillations: third harmonic injection (SVM used at the time)
In simulation
  Also look at the bode plot (not shown) to check phase margin

## Slide 15: GFL: Power step Change
Local oscillations: switching, resonance
Low frequency angle swing: controller
Mismatches: ESR of components
Results
2/4
15
Notes: Aim: control real and reactive power exchange. Hence power step change
Inverter 1 Open-Loop, Inverter 2 Closed Loop GFL
Comparison between simulation and hardware to verify validity of the model. Differences
  10kHz: switching noise
  1kHz: resonance
  Mismatch in low frequency angular swing – possibly due to mismatch in ESR leading to different controller compensation.
Comparison between different gains
  Larger kp fixe static error and increases slope of rise of first oscillation. But reduces time to accumulate error, leading to increased oscillation magnitudes
  Increasing Ki: faster Ki, at the cost of reduced phase margin, leading to more oscillations
Best response is t variable depending on application.
  Overall: 0.61,240 (red). best balance in terms of settling time and oscillation magnitude. Good for GFM when stability is required
  But 1.22 957 (green) might be a better starting point for GFL – faster response to regulate current controller quicker within the limits

## Slide 16: GFM: Voltage step change
Simulation time-step discretisation – Oscillations beyond sampling rate.
Conflicts between inner and outer loop bandwidth
Marginally stable pole from capacitor voltage dynamics
Results
3/4
16
Notes: GO OVER in 10 SECONDS
Not going through in as much detail (similar rationale)
GFM: control grid voltage and frequency. Here results for Vd step is shown

## Slide 17: Dual
Reduce integral gains of inner current loop to increase phase margin and stability (separation between loops)
Increase integral gain of voltage controller for reduced steady state error.
PLL response accelerated
Results
4/4
17
Notes: GO OVER in 10 SECONDS
INCREASE SEPARATION BETWEEN CUTOFF AND CROSSOVER FREQUENCIES
3 tests – combined testing of both in closed-loop
Reduce integral gains of current controller (increase inner loop phase margin and stability). Compensate for the bandwidth separation.
Increasing integral gain of GFM to reduce voltage steady state error and to speed up response
Accelerate PLL by increasing bandwidth and LPF cutoff frequency
Tuning is justified because it is done on real grids as well
with increased penetration of IBRs the synchronous mass is reducing (less stiff)
the dynamics is more reliant on the grid or load impedance
Overall: resilient to grid voltage and frequency perturbations, and can perform both as an importer or exporter.

## Slide 18: Conclusion
Dual-Inverter RCP System: deployment from simulation to hardware
Evaluation: Strengths and Limitations
  VS Simulations: Reflection of hardware sampling, discretisation and dynamics; but cannot reflect more complex systems
  VS High power systems: Safe but low power
Future works
  Small signal stability analysis
  Board optimisation: higher bandwidth op-amps, DC measurement accuracy, neutral terminal for damping tests
  Expansion: testing in parallel
Conclusion, Evaluation, Future Works
1/1
18
Notes: Proposal of RCP dual-inverter system: verified that the simulation and hardware results largely correspond.
Important: awareness for its limitations – discretisation in simulation, differences in low frequency oscillation due to parasitics mismatch (hard to measure)
Brings us to evaluation
  Compared to simulations: less flexibility in terms of cascading more blocks, for example to model solar irradiance effects. Hardware constraints reflected
  Compared to high power systems: more flexibility in real time control
Suitable for education and research purposes.
Future works
  Small signal stability analysis: so that it can work with a wider range of power perturbations (specifically at lower power) if unstable nodes are identified.
    Possible because we can model PI controller as a circuit impedance too
  Board optimisation: flexibility for higher slew rate and bandwidth op amp, DC measurement and damping (just to name a few)
  More high power tests – DC perturbation – facilitate studies with regards to driving renewable sources which are highly variable

## Slide 19: Thank you!
Now for the demo and then questions.
https://www.youtube.com/embed/VnrgIGNwcq8?mute=1;autoplay=1
19
Notes: <iframe width="560" height="315" src="https://www.youtube.com/embed/VnrgIGNwcq8" title="YouTube video player" frameborder="0" allow="accelerometer; autoplay; clipboard-write; encrypted-media; gyroscope; picture-in-picture; web-share" allowfullscreen></iframe>

## Slide 20: IBR Deployment on Present vs Future Grids
Introduction
Source: “Achieving a 100% Renewable Grid – Operating Electric Power Systems with Extremely High Levels of Variable Renewable Energy,” http://ieeexplore.ieee.org/document/7866938/
Notes: This brings us to the motivations of the projects
Paris agreement (net zero by 2050) – increasing RES
RES requires IBRs.
Deployment on present AC grids (with synchronous generation)
  vs future grids with more renewables. More IBRs and lower inertia
  Studying its characteristics/ stability

## Slide 21: 3-Phase DC-AC Half Bridge
SPWM (Sinusoidal PWM) strategy
Dead-time between switches
Offset by 120o to achieve a balanced 3-phase source
Hardware
2/5

## Slide 22: Filter
Objectives: Suppress ripples, harmonic distortion and EMI
L vs LC vs LCL
  Decrease inductor Lf size
  Up to 50% reduction in ripple magnitude of high frequency harmonics
  Decoupling measurement node from grid impedance
  Resonance frequency considerations: 1st vs 2nd vs 3rd order filter
Common Mode Choke
Hardware
3/5

## Slide 23: LCL Filter Parameters
Converter side inductor Lf – ripple current magnitude
Capacitor Cf – absorb high frequency switching frequency current
Grid-side inductor Lg – output current attenuation
Resonance Frequency Verification
Damping Resistor Rdamp – suppress resonance peak
Inverter Hardware
4/5

## Slide 24: CMC (Common Mode Choke)
Common Mode Voltage
ΔVCM difference between SPWM (sinusoidal PWM) and SVPWM (space-vector PWM) implementation
Rapid changes in ΔVCM leading to high pulsed common mode currents
Attenuation with CMC
  Flux created by the common-mode currents accumulate
  Produces an impedance that opposes the common-mode currents
  Noise returns to source via stray capacitances
Concerns: amount of attenuation, frequency of noise, losses, saturation
Hardware
5/5

## Slide 25: De-tour: PI Controller
Loop Shaping Method
Unity gain at crossover frequency
Separation between cutoff and crossover frequency
Control
2/7

## Slide 26: Specifications
DC Bus Voltage VDC 48V: Insulation cabinet not required
Nominal AC Voltage 30V: RMS
Nominal AC frequency 50Hz: Mains frequency
Nominal Phase Current 1.5A: Below 100W
Switching frequency fsw 10kHz: To match IGBT AC-DC Converters
Components
  Lf = 4 mH
  Cf = 8.8 μF
  Lg = 350 μH
Implementation
2/7
Notes: Skim over in 10 seconds

## Slide 27: Components
Implementation
3/7
3-Phase Inverter Module (“EVM”)
Load Resistor
Inverter Filter
Controller (“Simplus”)
16 channels: EPWM, ADC (voltage, current signals)
RTT (real time target) modification on MATLAB during runtime
Notes: Skim over in 30s
Mention Simplus: made by the laboratory, 16 channels
Allows modification of gains and real time gains on MATLAB during runtime

## Slide 28: Auxiliary Circuits: Vc Hall Voltage Measurement
Hall Effect Voltage Transducer LV 25-P Resistance Parameters
  Limit primary coil current (depends on maximum primary voltage)
  Scale secondary voltage with resistor
Implementation
4/7

## Slide 29: Auxiliary Circuits: Amplify EVM Measurements
Amplify 0-3.3V signals to ±15V to take full advantage of ± 2048 (digital)
Implementation
5/7

## Slide 30: Circuit Layout
Implementation
6/7
Notes: Circuit layout: also consisting of measurement circuitry

## Slide 31: Circuit: Overview for Signals
Implementation
7/7